## All Systems
Equipment | Type | Properties | Primary From | Alternate From
CHLB2100 | CHL | - | MSBBA110 | -
CRAB0300 | CRA | - | MDPBA110 | -
CRAB0403 | CRA | - | MDPBA110 | -
CRAB1003 | CRA | - | MDPBA110 | -
CRAB1004 | CRA | - | MDPBA110 | -
CRAB1603 | CRA | - | MDPBA110 | -
CRAB1604 | CRA | - | MDPBA110 | -
CRAB1900 | CRA | - | MDPBA110 | -
CRAB2200 | CRA | - | MDPBA110 | -
ELPBA110 | ELP | - | MDPBA110 | -
EPPBA120 | EPP | - | MDPBA110 | -
EPPBA230 | EPP | 480V:208Y/120, 45KVA, NEMA 1 | MDPBA110 | -
EPPBA320 | EPP | - | MDPBA110 | -
EPPBZ110 | EPP | - | MDPBA110 | -
EPPBZ210 | EPP | - | MDPBA110 | -
GENBA100 | GEN | 3000kW/3750KVA, 480Y/277V, 3 | - | -
GSBBA110 | GSB | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%, LSIG, ERMS, S.T.U. | GENBA100 | -
GSBBB110 | GSB | - | GSBBA110 | -
HUM00103 | HUM | - | MDPBA110 | -
MBCBA110 | MBC | 2500AF, 2500AT, 2500A, 480Y/277V, 3, , 3W, 100kAIC, 100%, LSI | UPSBA110 | UPBBA110
MDPBA110 | MDP | 600A, 480Y/277V, 3, , 3W, 65kAIC | MSBBA110 | -
MSBBA110 | MSB | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION, 4000AF, 4000AT, 100% | GSBBA110 | -
STSBA110 | STS | - | MBCBA110 | -
STSBA210 | STS | - | MBCBA110 | -
TRNBA110 | TRN | - | GSBBA110 | -
TRNBA210 | TRN | 480V:208Y/120, 45KVA, NEMA 1 | MDPBA110 | -
TRNBA310 | TRN | 480V:208Y/120, 75KVA, NEMA 1 | MDPBA110 | -
UDPBA310 | UDP | - | MBCBA110 | -
UPBBA110 | UPB | - | UPSBA110 | -
UPBBA120 | UPB | - | UPSBA210 | -
UPBBA210 | UPB | - | UPSBA110 | -
UPBBA220 | UPB | - | UPSBA210 | -
UPBBA310 | UPB | - | UPSBA110 | -
UPBBA320 | UPB | - | UPSBA210 | -
UPBBA410 | UPB | - | UPSBA110 | -
UPBBA420 | UPB | - | UPSBA210 | -
UPBBA510 | UPB | - | UPSBA110 | -
UPBBA520 | UPB | - | UPSBA210 | -
UPSBA110 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MSBBA110 | -
UPSBA210 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MDPBA110 | -
ATSBA130 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBA230 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBA330 | ATS | 800A,480V, 3 | BSWBZ310 | -
ATSBA430 | ATS | 800A,480V, 3 | BSWBZ310 | -
BSWBZ110 | BSW | - | MBCBA110 | -
BSWBZ210 | BSW | - | UDPBA310 | -
BSWBZ310 | BSW | - | RPPBA174 | -
MBCBA110 | MBC | - | - | -
PDUBA110 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | STSBA110 | -
PDUBA210 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBA130 | -
PDUBA310 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBA110 | -
PDUBA420 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBA230 | -
PDUBA520 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBA220 | -
PDUBA630 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBA330 | -
PDUBA720 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBA220 | -
PDUBA840 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBA430 | -
RPPBA113 | RPP | - | PDUBA110 | -
RPPBA123 | RPP | - | PDUBA210 | -
RPPBA133 | RPP | - | PDUBA310 | -
RPPBA143 | RPP | - | PDUBA420 | -
RPPBA154 | RPP | - | PDUBA520 | -
RPPBA164 | RPP | - | PDUBA630 | -
RPPBA174 | RPP | - | PDUBA720 | -
RPPBA184 | RPP | - | PDUBA840 | -
RPPBA213 | RPP | - | PDUBA110 | -
RPPBA223 | RPP | - | PDUBA210 | -
RPPBA233 | RPP | - | PDUBA310 | -
RPPBA243 | RPP | - | PDUBA420 | -
RPPBA254 | RPP | - | PDUBA520 | -
RPPBA264 | RPP | - | PDUBA630 | -
RPPBA274 | RPP | - | PDUBA720 | -
RPPBA284 | RPP | - | PDUBA840 | -
RPPBA313 | RPP | - | PDUBA110 | -
RPPBA323 | RPP | - | PDUBA210 | -
RPPBA333 | RPP | - | PDUBA310 | -
RPPBA343 | RPP | - | PDUBA420 | -
RPPBA354 | RPP | - | PDUBA520 | -
RPPBA364 | RPP | - | PDUBA630 | -
RPPBA374 | RPP | - | PDUBA720 | -
RPPBA384 | RPP | - | PDUBA840 | -
RPPBA413 | RPP | - | PDUBA110 | -
RPPBA423 | RPP | - | PDUBA210 | -
RPPBA433 | RPP | - | PDUBA310 | -
RPPBA443 | RPP | - | PDUBA420 | -
RPPBA454 | RPP | - | PDUBA520 | -
RPPBA464 | RPP | - | PDUBA630 | -
RPPBA474 | RPP | - | PDUBA720 | -
RPPBA484 | RPP | - | PDUBA840 | -
RPPBA513 | RPP | 250A, 415Y/240V, 3, , 4W, 18kAIC | PDUBA110 | -
RPPBA523 | RPP | 250A, 415Y/240V, 3 | PDUBA210 | -
RPPBA533 | RPP | - | PDUBA310 | -
RPPBA543 | RPP | 250A, 415Y/240V, 3 | PDUBA420 | -
RPPBA554 | RPP | - | PDUBA520 | -
RPPBA564 | RPP | 250A, 415Y/240V, 3 | PDUBA630 | -
RPPBA574 | RPP | - | PDUBA720 | -
RPPBA584 | RPP | 250A, 415Y/240V, 3 | PDUBA840 | -
RPPBA610 | RPP | - | PDUBA310 | -
STSBA110 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
STSBA210 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
TRNBA410 | TRN | - | PDUBA310 | -
UDPBA110 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF, 800A | STSBA110 | -
UDPBA220 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF | STSBA210 | -
UDPBA310 | UDP | 2500A, 480V, 3, , 3W, 65kAIC, 800AF, 800AT | RPPBA154 | -
CHLB2000 | CHL | - | MSBBB110 | -
CRAB0200 | CRA | - | MDPBB110 | -
CRAB0303 | CRA | - | MDPBB110 | -
CRAB0903 | CRA | - | MDPBB110 | -
CRAB0904 | CRA | - | MDPBB110 | -
CRAB1503 | CRA | - | MDPBB110 | -
CRAB1504 | CRA | - | MDPBB110 | -
CRAB2000 | CRA | - | MDPBB110 | -
CRAB2100 | CRA | - | MDPBB110 | -
ELPBB110 | ELP | PANEL | MDPBB110 | -
ELPBB240 | ELP | - | MDPBB110 | -
EPPBB120 | EPP | - | MDPBB110 | -
EPPBB230 | EPP | - | MDPBB110 | -
EPPBZ110 | EPP | - | MDPBB110 | -
EPPBZ210 | EPP | - | MDPBB110 | -
GENBB100 | GEN | 3000kW/3750KVA, 480Y/277V, 3 | - | -
GSBBA110 | GSB | - | GSBBB110 | -
GSBBB110 | GSB | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%, LSIG, ERMS, S.T.U. | GENBB100 | -
GSBBC110 | GSB | - | GSBBB110 | -
HUM00203 | HUM | - | MDPBB110 | -
MBCBB110 | MBC | 2500AF, 2500AT, 2500A, 480Y/277V, 3, , 3W, 100kAIC, 100%, LSI | UPSBB110 | -
MDPBB110 | MDP | 600A, 480Y/277V, 3, , 3W, 65kAIC | MSBBB110 | -
MSBBB110 | MSB | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION, 4000AF, 4000AT, 100% | GSBBB110 | GENBB100
STSBB110 | STS | - | MBCBB110 | -
STSBB210 | STS | - | MBCBB110 | -
TRNBB110 | TRN | - | GSBBB110 | -
TRNBB210 | TRN | 480V:208Y/120, 45KVA, NEMA 1, PANEL | MDPBB110 | -
TRNBB310 | TRN | - | MDPBB110 | -
TRNBB410 | TRN | 480V:480Y/277, 30KVA, NEMA 1 | MDPBB110 | -
UDPBB310 | UDP | - | MBCBB110 | -
UPBBB110 | UPB | - | UPSBB110 | -
UPBBB120 | UPB | - | UPSBB210 | -
UPBBB210 | UPB | - | UPSBB110 | -
UPBBB220 | UPB | - | UPSBB210 | -
UPBBB310 | UPB | - | UPSBB110 | -
UPBBB320 | UPB | - | UPSBB210 | -
UPBBB410 | UPB | - | UPSBB110 | -
UPBBB420 | UPB | - | UPSBB210 | -
UPBBB510 | UPB | - | UPSBB110 | -
UPBBB520 | UPB | - | UPSBB210 | -
UPSBB110 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MSBBB110 | -
UPSBB210 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MDPBB110 | -
ATSBB130 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBB230 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBB330 | ATS | 800A,480V, 3 | BSWBZ310 | BSWBZ210
ATSBB430 | ATS | 800A,480V, 3 | UDPBB310 | BSWBZ310
BSWBZ110 | BSW | - | MBCBB110 | -
BSWBZ210 | BSW | - | UDPBB310 | -
BSWBZ310 | BSW | - | UDPBB310 | -
MBCBB110 | MBC | - | - | -
PDUBB110 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | STSBB110 | -
PDUBB210 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBB130 | -
PDUBB310 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBB110 | -
PDUBB420 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBB230 | -
PDUBB520 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBB220 | -
PDUBB630 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBB330 | -
PDUBB720 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBB220 | -
PDUBB840 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBB430 | -
RPPBB113 | RPP | - | PDUBB310 | -
RPPBB123 | RPP | - | PDUBB210 | -
RPPBB133 | RPP | - | PDUBB520 | -
RPPBB143 | RPP | - | PDUBB420 | -
RPPBB154 | RPP | - | PDUBB520 | -
RPPBB164 | RPP | - | PDUBB840 | -
RPPBB174 | RPP | - | PDUBB720 | -
RPPBB184 | RPP | - | PDUBB840 | -
RPPBB213 | RPP | - | PDUBB310 | -
RPPBB223 | RPP | - | PDUBB210 | -
RPPBB233 | RPP | - | PDUBB520 | -
RPPBB243 | RPP | - | PDUBB420 | -
RPPBB254 | RPP | - | PDUBB520 | -
RPPBB264 | RPP | - | PDUBB840 | -
RPPBB274 | RPP | - | PDUBB720 | -
RPPBB284 | RPP | - | PDUBB840 | -
RPPBB313 | RPP | - | PDUBB310 | -
RPPBB323 | RPP | - | PDUBB210 | -
RPPBB333 | RPP | - | PDUBB520 | -
RPPBB343 | RPP | - | PDUBB420 | -
RPPBB354 | RPP | - | PDUBB520 | -
RPPBB364 | RPP | - | PDUBB840 | -
RPPBB374 | RPP | - | PDUBB720 | -
RPPBB384 | RPP | - | PDUBB840 | -
RPPBB413 | RPP | - | PDUBB310 | -
RPPBB423 | RPP | - | PDUBB210 | -
RPPBB433 | RPP | - | PDUBB520 | -
RPPBB443 | RPP | - | PDUBB420 | -
RPPBB454 | RPP | - | PDUBB520 | -
RPPBB464 | RPP | - | PDUBB840 | -
RPPBB474 | RPP | - | PDUBB720 | -
RPPBB484 | RPP | - | PDUBB840 | -
RPPBB513 | RPP | 250A, 415Y/240V, 3, , 4W, 18kAIC | PDUBB310 | -
RPPBB523 | RPP | 250A, 415Y/240V, 3 | PDUBB210 | -
RPPBB533 | RPP | - | PDUBB520 | -
RPPBB543 | RPP | 250A, 415Y/240V, 3 | PDUBB420 | -
RPPBB554 | RPP | - | PDUBB520 | -
RPPBB564 | RPP | 250A, 415Y/240V, 3 | PDUBB840 | -
RPPBB574 | RPP | - | PDUBB720 | -
RPPBB584 | RPP | 250A, 415Y/240V, 3 | PDUBB840 | -
RPPBB650 | RPP | - | PDUBB720 | -
STSBB110 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
STSBB210 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
TRNBB550 | TRN | 100%, 415V:208Y/120 | PDUBB720 | -
UDPBB110 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF | STSBB110 | -
UDPBB220 | UDP | 1600A, 480V, 3, , 3W, 65kAIC | STSBB210 | -
UDPBB310 | UDP | 2500A, 480V, 3, , 3W, 65kAIC, 800AF, 800AT | RPPBB154 | -
CHLB1900 | CHL | - | MSBBC110 | -
CRAB0100 | CRA | - | MDPBC110 | -
CRAB0203 | CRA | - | MDPBC110 | -
CRAB0404 | CRA | - | MDPBC110 | -
CRAB0803 | CRA | - | MDPBC110 | -
CRAB0804 | CRA | - | MDPBC110 | -
CRAB1403 | CRA | - | MDPBC110 | -
CRAB1404 | CRA | - | MDPBC110 | -
CRAB2300 | CRA | - | MDPBC110 | -
CRAB2800 | CRA | - | MDPBC110 | -
ELPBC110 | ELP | - | MDPBC110 | -
ELPBC230 | ELP | - | MDPBC110 | -
EPPBC120 | EPP | - | MDPBC110 | -
EPPBZ110 | EPP | - | MDPBC110 | -
EPPBZ210 | EPP | - | MDPBC110 | -
GENBC100 | GEN | 3000kW/3750KVA, 480Y/277V, 3 | - | -
GSBBB110 | GSB | - | GSBBC110 | -
GSBBC110 | GSB | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%, LSIG, ERMS, S.T.U. | GENBC100 | -
GSBBZ110 | GSB | - | GSBBC110 | -
HUM00303 | HUM | - | MDPBC110 | -
MBCBC110 | MBC | 2500AF, 2500AT, 2500A, 480Y/277V, 3, , 3W, 100kAIC, 100%, LSI | UPSBC110 | UPBBC110
MDPBC110 | MDP | 600A, 480Y/277V, 3, , 3W, 65kAIC | MSBBC110 | -
MSBBC110 | MSB | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION, 4000AF, 4000AT, 100% | GSBBC110 | -
STSBC110 | STS | - | MBCBC110 | -
STSBC210 | STS | - | MBCBC110 | -
TRNBC110 | TRN | - | GSBBC110 | -
TRNBC210 | TRN | 480V:208Y/120, 45KVA, NEMA 1, PANEL | MDPBC110 | -
TRNBC310 | TRN | 480V:480Y/277, 30KVA, NEMA 1 | MDPBC110 | -
UDPBC310 | UDP | - | MBCBC110 | -
UPBBC110 | UPB | - | UPSBC110 | -
UPBBC120 | UPB | - | UPSBC210 | -
UPBBC210 | UPB | - | UPSBC110 | -
UPBBC220 | UPB | - | UPSBC210 | -
UPBBC310 | UPB | - | UPSBC110 | -
UPBBC320 | UPB | - | UPSBC210 | -
UPBBC410 | UPB | - | UPSBC110 | -
UPBBC420 | UPB | - | UPSBC210 | -
UPBBC510 | UPB | - | UPSBC110 | -
UPBBC520 | UPB | - | UPSBC210 | -
UPSBC110 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MSBBC110 | -
UPSBC210 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MDPBC110 | -
ATSBC130 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBC230 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBC330 | ATS | 800A,480V, 3 | BSWBZ310 | BSWBZ210
ATSBC430 | ATS | 800A,480V, 3 | BSWBZ310 | -
BSWBZ110 | BSW | - | MBCBC110 | -
BSWBZ210 | BSW | - | UDPBC310 | -
BSWBZ310 | BSW | - | RPPBC174 | -
MBCBC110 | MBC | - | - | -
PDUBC110 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | STSBC110 | -
PDUBC210 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | ATSBC130 | -
PDUBC310 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | UDPBC110 | -
PDUBC420 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | ATSBC230 | -
PDUBC520 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | UDPBC220 | -
PDUBC630 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | ATSBC330 | -
PDUBC720 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | UDPBC220 | -
PDUBC840 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | ATSBC430 | -
RPPBC113 | RPP | - | PDUBC110 | -
RPPBC123 | RPP | - | PDUBC210 | -
RPPBC133 | RPP | - | PDUBC310 | -
RPPBC143 | RPP | - | PDUBC420 | -
RPPBC154 | RPP | - | PDUBC520 | -
RPPBC164 | RPP | - | PDUBC630 | -
RPPBC174 | RPP | - | PDUBC720 | -
RPPBC184 | RPP | - | PDUBC840 | -
RPPBC213 | RPP | - | PDUBC110 | -
RPPBC223 | RPP | - | PDUBC210 | -
RPPBC233 | RPP | - | PDUBC310 | -
RPPBC243 | RPP | - | PDUBC420 | -
RPPBC254 | RPP | - | PDUBC520 | -
RPPBC264 | RPP | - | PDUBC630 | -
RPPBC274 | RPP | - | PDUBC720 | -
RPPBC284 | RPP | - | PDUBC840 | -
RPPBC313 | RPP | - | PDUBC110 | -
RPPBC323 | RPP | - | PDUBC210 | -
RPPBC333 | RPP | - | PDUBC310 | -
RPPBC343 | RPP | - | PDUBC420 | -
RPPBC354 | RPP | - | PDUBC520 | -
RPPBC364 | RPP | - | PDUBC630 | -
RPPBC374 | RPP | - | PDUBC720 | -
RPPBC384 | RPP | - | PDUBC840 | -
RPPBC413 | RPP | - | PDUBC110 | -
RPPBC423 | RPP | - | PDUBC210 | -
RPPBC433 | RPP | - | PDUBC310 | -
RPPBC443 | RPP | - | PDUBC420 | -
RPPBC454 | RPP | - | PDUBC520 | -
RPPBC464 | RPP | - | PDUBC630 | -
RPPBC474 | RPP | - | PDUBC720 | -
RPPBC484 | RPP | - | PDUBC840 | -
RPPBC513 | RPP | 250A, 415Y/240V, 3, , 4W, 18kAIC | PDUBC110 | -
RPPBC523 | RPP | 250A, 415Y/240V, 3 | PDUBC210 | -
RPPBC533 | RPP | - | PDUBC310 | -
RPPBC543 | RPP | 250A, 415Y/240V, 3 | PDUBC420 | -
RPPBC554 | RPP | - | PDUBC520 | -
RPPBC564 | RPP | 250A, 415Y/240V, 3 | PDUBC630 | -
RPPBC574 | RPP | - | PDUBC720 | -
RPPBC584 | RPP | 250A, 415Y/240V, 3 | PDUBC840 | -
STSBC110 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
STSBC210 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
UDPBC110 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF, 800A | STSBC110 | -
UDPBC220 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF | STSBC210 | -
UDPBC310 | UDP | 2500A, 480V, 3, , 3W, 65kAIC, 800AF, 800AT | RPPBC154 | -
CHLB1700 | CHL | - | MSBBD110 | -
CRAB0103 | CRA | - | MDPBD110 | -
CRAB0304 | CRA | - | MDPBD110 | -
CRAB0600 | CRA | - | MDPBD110 | -
CRAB0703 | CRA | - | MDPBD110 | -
CRAB0704 | CRA | - | MDPBD110 | -
CRAB1303 | CRA | - | MDPBD110 | -
CRAB1304 | CRA | - | MDPBD110 | -
CRAB2600 | CRA | - | MDPBD110 | -
CRAB2700 | CRA | - | MDPBD110 | -
ELPBD110 | ELP | - | MDPBD110 | -
ELPBD230 | ELP | - | MDPBD110 | -
EPPBD120 | EPP | - | MDPBD110 | -
EPPBZ110 | EPP | - | MDPBD110 | -
EPPBZ210 | EPP | - | MDPBD110 | -
GENBD100 | GEN | 3000kW/3750KVA, 480Y/277V, 3 | - | -
GSBBD110 | GSB | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%, LSIG, ERMS, S.T.U. | GENBD100 | -
GSBBE110 | GSB | - | GSBBD110 | -
GSBBZ110 | GSB | - | GSBBD110 | -
HUM00304 | HUM | - | MDPBD110 | -
MBCBD110 | MBC | 2500AF, 2500AT, 2500A, 480Y/277V, 3, , 3W, 100kAIC, 100%, LSI | UPSBD110 | -
MDPBD110 | MDP | 600A, 480Y/277V, 3, , 3W, 65kAIC | MSBBD110 | -
MSBBD110 | MSB | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION, 4000AF, 4000AT, 100% | GSBBD110 | GENBD100
STSBD110 | STS | - | MBCBD110 | -
STSBD210 | STS | - | MBCBD110 | -
TRNBD110 | TRN | - | GSBBD110 | -
TRNBD210 | TRN | 480V:208Y/120, 45KVA, NEMA 1, PANEL | MDPBD110 | -
TRNBD310 | TRN | 480V:480Y/277, 30KVA, NEMA 1 | MDPBD110 | -
UDPBD310 | UDP | - | MBCBD110 | -
UPBBD110 | UPB | - | UPSBD110 | -
UPBBD120 | UPB | - | UPSBD210 | -
UPBBD210 | UPB | - | UPSBD110 | -
UPBBD220 | UPB | - | UPSBD210 | -
UPBBD310 | UPB | - | UPSBD110 | -
UPBBD320 | UPB | - | UPSBD210 | -
UPBBD410 | UPB | - | UPSBD110 | -
UPBBD420 | UPB | - | UPSBD210 | -
UPBBD510 | UPB | - | UPSBD110 | -
UPBBD520 | UPB | - | UPSBD210 | -
UPSBD110 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MSBBD110 | -
UPSBD210 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MDPBD110 | -
ATSBD130 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBD230 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBD330 | ATS | 800A,480V, 3 | BSWBZ310 | BSWBZ210
ATSBD430 | ATS | 800A,480V, 3 | UDPBD310 | BSWBZ310
BSWBZ110 | BSW | - | MBCBD110 | -
BSWBZ210 | BSW | - | UDPBD310 | -
BSWBZ310 | BSW | - | UDPBD310 | -
MBCBD110 | MBC | - | - | -
PDUBD110 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | STSBD110 | -
PDUBD210 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | ATSBD130 | -
PDUBD310 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | UDPBD110 | -
PDUBD420 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | ATSBD230 | -
PDUBD520 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | UDPBD220 | -
PDUBD630 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | ATSBD330 | -
PDUBD720 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | UDPBD220 | -
PDUBD840 | PDU | 500KVA, 480V:415Y/240V, 65kAIC | ATSBD430 | -
RPPBD113 | RPP | - | PDUBD310 | -
RPPBD123 | RPP | - | PDUBD210 | -
RPPBD133 | RPP | - | PDUBD520 | -
RPPBD143 | RPP | - | PDUBD420 | -
RPPBD154 | RPP | - | PDUBD520 | -
RPPBD164 | RPP | - | PDUBD840 | -
RPPBD174 | RPP | - | PDUBD720 | -
RPPBD184 | RPP | - | PDUBD840 | -
RPPBD213 | RPP | - | PDUBD310 | -
RPPBD223 | RPP | - | PDUBD210 | -
RPPBD233 | RPP | - | PDUBD520 | -
RPPBD243 | RPP | - | PDUBD420 | -
RPPBD254 | RPP | - | PDUBD520 | -
RPPBD264 | RPP | - | PDUBD840 | -
RPPBD274 | RPP | - | PDUBD720 | -
RPPBD284 | RPP | - | PDUBD840 | -
RPPBD313 | RPP | - | PDUBD310 | -
RPPBD323 | RPP | - | PDUBD210 | -
RPPBD333 | RPP | - | PDUBD520 | -
RPPBD343 | RPP | - | PDUBD420 | -
RPPBD354 | RPP | - | PDUBD520 | -
RPPBD364 | RPP | - | PDUBD840 | -
RPPBD374 | RPP | - | PDUBD720 | -
RPPBD384 | RPP | - | PDUBD840 | -
RPPBD413 | RPP | - | PDUBD310 | -
RPPBD423 | RPP | - | PDUBD210 | -
RPPBD433 | RPP | - | PDUBD520 | -
RPPBD443 | RPP | - | PDUBD420 | -
RPPBD454 | RPP | - | PDUBD520 | -
RPPBD464 | RPP | - | PDUBD840 | -
RPPBD474 | RPP | - | PDUBD720 | -
RPPBD484 | RPP | - | PDUBD840 | -
RPPBD513 | RPP | 250A, 415Y/240V, 3, , 4W, 18kAIC | PDUBD310 | -
RPPBD523 | RPP | 250A, 415Y/240V, 3 | PDUBD210 | -
RPPBD533 | RPP | - | PDUBD520 | -
RPPBD543 | RPP | 250A, 415Y/240V, 3 | PDUBD420 | -
RPPBD554 | RPP | - | PDUBD520 | -
RPPBD564 | RPP | 250A, 415Y/240V, 3 | PDUBD840 | -
RPPBD574 | RPP | - | PDUBD720 | -
RPPBD584 | RPP | 250A, 415Y/240V, 3 | PDUBD840 | -
STSBD110 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
STSBD210 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
UDPBD110 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF, 800A | STSBD110 | -
UDPBD220 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF | STSBD210 | -
UDPBD310 | UDP | 2500A, 480V, 3, , 3W, 65kAIC, 800AF, 800AT | RPPBD154 | -
CHLB1600 | CHL | - | MSBBE110 | -
CRAB0204 | CRA | - | MDPBE110 | -
CRAB0500 | CRA | - | MDPBE110 | -
CRAB0603 | CRA | - | MDPBE110 | -
CRAB0604 | CRA | - | MDPBE110 | -
CRAB1203 | CRA | - | MDPBE110 | -
CRAB1204 | CRA | - | MDPBE110 | -
CRAB2900 | CRA | - | MDPBE110 | -
CRAB3200 | CRA | - | MDPBE110 | -
ELPBE110 | ELP | - | MDPBE110 | -
ELPBE230 | ELP | - | MDPBE110 | -
EPPBE120 | EPP | - | MDPBE110 | -
EPPBZ110 | EPP | - | MDPBE110 | -
EPPBZ210 | EPP | - | MDPBE110 | -
GENBE100 | GEN | 3000kW/3750KVA, 480Y/277V, 3 | - | -
GSBBD110 | GSB | - | GSBBE110 | -
GSBBE110 | GSB | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%, LSIG, ERMS, S.T.U. | GENBE100 | -
GSBBF110 | GSB | - | GSBBE110 | -
HUM00204 | HUM | - | MDPBE110 | -
MBCBE110 | MBC | 2500AF, 2500AT, 2500A, 480Y/277V, 3, , 3W, 100kAIC, 100%, LSI | UPSBE110 | -
MDPBE110 | MDP | 600A, 480Y/277V, 3, , 3W, 65kAIC | MSBBE110 | -
MSBBE110 | MSB | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION, 4000AF, 4000AT, 100% | GSBBE110 | GENBE100
STSBE110 | STS | - | MBCBE110 | -
STSBE210 | STS | - | MBCBE110 | -
TRNBE110 | TRN | - | GSBBE110 | -
TRNBE210 | TRN | 480V:208Y/120, 45KVA, NEMA 1, PANEL | MDPBE110 | -
TRNBE310 | TRN | 480V:480Y/277, 30KVA, NEMA 1 | MDPBE110 | -
UDPBE310 | UDP | - | MBCBE110 | -
UPBBE110 | UPB | - | UPSBE110 | -
UPBBE120 | UPB | - | UPSBE210 | -
UPBBE210 | UPB | - | UPSBE110 | -
UPBBE220 | UPB | - | UPSBE210 | -
UPBBE310 | UPB | - | UPSBE110 | -
UPBBE320 | UPB | - | UPSBE210 | -
UPBBE410 | UPB | - | UPSBE110 | -
UPBBE420 | UPB | - | UPSBE210 | -
UPBBE510 | UPB | - | UPSBE110 | -
UPBBE520 | UPB | - | UPSBE210 | -
UPSBE110 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MSBBE110 | -
UPSBE210 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MDPBE110 | -
ATSBE130 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBE230 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBE330 | ATS | 800A,480V, 3 | BSWBZ310 | BSWBZ210
ATSBE430 | ATS | 800A,480V, 3 | UDPBE310 | BSWBZ310
BSWBZ110 | BSW | - | MBCBE110 | -
BSWBZ210 | BSW | - | UDPBE310 | -
BSWBZ310 | BSW | - | UDPBE310 | -
MBCBE110 | MBC | - | - | -
PDUBE110 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | STSBE110 | -
PDUBE210 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBE130 | -
PDUBE310 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBE110 | -
PDUBE420 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBE230 | -
PDUBE520 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBE220 | -
PDUBE630 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBE330 | -
PDUBE720 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBE220 | -
PDUBE840 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBE430 | -
RPPBE113 | RPP | - | PDUBE310 | -
RPPBE123 | RPP | - | PDUBE210 | -
RPPBE133 | RPP | - | PDUBE520 | -
RPPBE143 | RPP | - | PDUBE420 | -
RPPBE154 | RPP | - | PDUBE520 | -
RPPBE164 | RPP | - | PDUBE840 | -
RPPBE174 | RPP | - | PDUBE720 | -
RPPBE184 | RPP | - | PDUBE840 | -
RPPBE213 | RPP | - | PDUBE310 | -
RPPBE223 | RPP | - | PDUBE210 | -
RPPBE233 | RPP | - | PDUBE520 | -
RPPBE243 | RPP | - | PDUBE420 | -
RPPBE254 | RPP | - | PDUBE520 | -
RPPBE264 | RPP | - | PDUBE840 | -
RPPBE274 | RPP | - | PDUBE720 | -
RPPBE284 | RPP | - | PDUBE840 | -
RPPBE313 | RPP | - | PDUBE310 | -
RPPBE323 | RPP | - | PDUBE210 | -
RPPBE333 | RPP | - | PDUBE520 | -
RPPBE343 | RPP | - | PDUBE420 | -
RPPBE354 | RPP | - | PDUBE520 | -
RPPBE364 | RPP | - | PDUBE840 | -
RPPBE374 | RPP | - | PDUBE720 | -
RPPBE384 | RPP | - | PDUBE840 | -
RPPBE413 | RPP | - | PDUBE310 | -
RPPBE423 | RPP | - | PDUBE210 | -
RPPBE433 | RPP | - | PDUBE520 | -
RPPBE443 | RPP | - | PDUBE420 | -
RPPBE454 | RPP | - | PDUBE520 | -
RPPBE464 | RPP | - | PDUBE840 | -
RPPBE474 | RPP | - | PDUBE720 | -
RPPBE484 | RPP | - | PDUBE840 | -
RPPBE513 | RPP | 250A, 415Y/240V, 3, , 4W, 18kAIC | PDUBE310 | -
RPPBE523 | RPP | 250A, 415Y/240V, 3 | PDUBE210 | -
RPPBE533 | RPP | - | PDUBE520 | -
RPPBE543 | RPP | 250A, 415Y/240V, 3 | PDUBE420 | -
RPPBE554 | RPP | - | PDUBE520 | -
RPPBE564 | RPP | 250A, 415Y/240V, 3 | PDUBE840 | -
RPPBE574 | RPP | - | PDUBE720 | -
RPPBE584 | RPP | 250A, 415Y/240V, 3 | PDUBE840 | -
RPPBE650 | RPP | - | PDUBE720 | -
RPPBE760 | RPP | 800AF, 800A, 800AT | UDPBE310 | -
STSBE110 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
STSBE210 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
TRNBE450 | TRN | 100%, 415V:208Y/120 | PDUBE720 | -
UDPBE110 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF | STSBE110 | -
UDPBE220 | UDP | 1600A, 480V, 3, , 3W, 65kAIC | STSBE210 | -
UDPBE310 | UDP | 2500A, 480V, 3, , 3W, 65kAIC, 800AF, 800AT | RPPBE154 | -
BSW00200 | BSW | - | GSBBF110 | -
CHLB1500 | CHL | - | MSBBF110 | -
CRAB0104 | CRA | - | MDPBF110 | -
CRAB0400 | CRA | - | MDPBF110 | -
CRAB0503 | CRA | - | MDPBF110 | -
CRAB0504 | CRA | - | MDPBF110 | -
CRAB1103 | CRA | - | MDPBF110 | -
CRAB1104 | CRA | - | MDPBF110 | -
CRAB3000 | CRA | - | MDPBF110 | -
CRAB3100 | CRA | - | MDPBF110 | -
ELPBF110 | ELP | - | MDPBF110 | -
EPPBF120 | EPP | - | MDPBF110 | -
EPPBF230 | EPP | 480V:208Y/120, 45KVA, NEMA 1 | MDPBF110 | -
EPPBF320 | EPP | - | MDPBF110 | -
EPPBZ110 | EPP | - | MDPBF110 | -
EPPBZ210 | EPP | - | MDPBF110 | -
GENBF100 | GEN | 3000kW/3750KVA, 480Y/277V, 3 | - | -
GSBBE110 | GSB | - | GSBBF110 | -
GSBBF110 | GSB | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%, LSIG, ERMS, S.T.U. | GENBF100 | -
HUM00104 | HUM | - | MDPBF110 | -
MBCBF110 | MBC | 2500AF, 2500AT, 2500A, 480Y/277V, 3, , 3W, 100kAIC, 100%, LSI | UPSBF110 | -
MDPBF110 | MDP | 600A, 480Y/277V, 3, , 3W, 65kAIC | MSBBF110 | -
MSBBF110 | MSB | 4000A, 480Y/277V, 3, WOODWARD PLC BREAKER TRANSFER CONTROLLER, , 4W, 100kAIC, S.E. RATED, BREAKER TRANSFER IS DELAYED OPEN TRANSITION, 4000AF, 4000AT, 100% | GSBBF110 | GENBF100
STSBF110 | STS | - | MBCBF110 | -
STSBF210 | STS | - | MBCBF110 | -
TRNBF110 | TRN | - | GSBBF110 | -
TRNBF210 | TRN | 480V:208Y/120, 45KVA, NEMA 1 | MDPBF110 | -
TRNBF310 | TRN | - | MDPBF110 | -
UDPBF310 | UDP | - | MBCBF110 | -
UPBBF110 | UPB | - | UPSBF110 | -
UPBBF120 | UPB | - | UPSBF210 | -
UPBBF210 | UPB | - | UPSBF110 | -
UPBBF220 | UPB | - | UPSBF210 | -
UPBBF310 | UPB | - | UPSBF110 | -
UPBBF320 | UPB | - | UPSBF210 | -
UPBBF410 | UPB | - | UPSBF110 | -
UPBBF420 | UPB | - | UPSBF210 | -
UPBBF510 | UPB | - | UPSBF110 | -
UPBBF520 | UPB | - | UPSBF210 | -
UPSBF110 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MSBBF110 | -
UPSBF210 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MDPBF110 | -
ATSBF130 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBF230 | ATS | 800A,480V, 3 | BSWBZ210 | -
ATSBF330 | ATS | 800A,480V, 3 | BSWBZ310 | BSWBZ210
ATSBF430 | ATS | 800A,480V, 3 | UDPBF310 | BSWBZ310
BSWBZ110 | BSW | - | MBCBF110 | -
BSWBZ210 | BSW | - | UDPBF310 | -
BSWBZ310 | BSW | - | UDPBF310 | -
MBCBF110 | MBC | - | - | -
PDUBF110 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | STSBF110 | -
PDUBF210 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBF130 | -
PDUBF310 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBF110 | -
PDUBF420 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBF230 | -
PDUBF520 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBF220 | -
PDUBF630 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBF330 | -
PDUBF720 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | UDPBF220 | -
PDUBF840 | PDU | 500KVA, K4 RATING, 480V:415Y/240V, 65kAIC | ATSBF430 | -
RPPBF113 | RPP | - | PDUBF310 | -
RPPBF123 | RPP | - | PDUBF210 | -
RPPBF133 | RPP | - | PDUBF520 | -
RPPBF143 | RPP | - | PDUBF420 | -
RPPBF154 | RPP | - | PDUBF520 | -
RPPBF164 | RPP | - | PDUBF840 | -
RPPBF174 | RPP | - | PDUBF720 | -
RPPBF184 | RPP | - | PDUBF840 | -
RPPBF213 | RPP | - | PDUBF310 | -
RPPBF223 | RPP | - | PDUBF210 | -
RPPBF233 | RPP | - | PDUBF520 | -
RPPBF243 | RPP | - | PDUBF420 | -
RPPBF254 | RPP | - | PDUBF520 | -
RPPBF264 | RPP | - | PDUBF840 | -
RPPBF274 | RPP | - | PDUBF720 | -
RPPBF284 | RPP | - | PDUBF840 | -
RPPBF313 | RPP | - | PDUBF310 | -
RPPBF323 | RPP | - | PDUBF210 | -
RPPBF333 | RPP | - | PDUBF520 | -
RPPBF343 | RPP | - | PDUBF420 | -
RPPBF354 | RPP | - | PDUBF520 | -
RPPBF364 | RPP | - | PDUBF840 | -
RPPBF374 | RPP | - | PDUBF720 | -
RPPBF384 | RPP | - | PDUBF840 | -
RPPBF413 | RPP | - | PDUBF310 | -
RPPBF423 | RPP | - | PDUBF210 | -
RPPBF433 | RPP | - | PDUBF520 | -
RPPBF443 | RPP | - | PDUBF420 | -
RPPBF454 | RPP | - | PDUBF520 | -
RPPBF464 | RPP | - | PDUBF840 | -
RPPBF474 | RPP | - | PDUBF720 | -
RPPBF484 | RPP | - | PDUBF840 | -
RPPBF513 | RPP | 250A, 415Y/240V, 3, , 4W, 18kAIC | PDUBF310 | -
RPPBF523 | RPP | 250A, 415Y/240V, 3 | PDUBF210 | -
RPPBF533 | RPP | - | PDUBF520 | -
RPPBF543 | RPP | 250A, 415Y/240V, 3 | PDUBF420 | -
RPPBF554 | RPP | - | PDUBF520 | -
RPPBF564 | RPP | 250A, 415Y/240V, 3 | PDUBF840 | -
RPPBF574 | RPP | - | PDUBF720 | -
RPPBF584 | RPP | 250A, 415Y/240V, 3 | PDUBF840 | -
RPPBF610 | RPP | - | PDUBF310 | -
RPPBF760 | RPP | - | PDUBF310 | -
STSBF110 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
STSBF210 | STS | 1600A, 480V, 3, 3 POLE, 65kAIC | BSWBZ110 | -
TRNBF410 | TRN | 100%, 415V:208Y/120 | PDUBF310 | -
UDPBF110 | UDP | 1600A, 480V, 3, , 3W, 65kAIC, 800AF | STSBF110 | -
UDPBF220 | UDP | 1600A, 480V, 3, , 3W, 65kAIC | STSBF210 | -
UDPBF310 | UDP | 2500A, 480V, 3, , 3W, 65kAIC, 800AF, 800AT | RPPBF154 | -
AHU00100 | AHU | - | GENBH100 | -
AHU00200 | AHU | - | GENBH100 | -
AHU04100 | AHU | - | GENBH100 | -
AHU04300 | AHU | - | GENBH100 | -
AHU04600 | AHU | - | GENBH100 | -
AHU04800 | AHU | - | GENBH100 | -
ATSBH110 | ATS | 2500AF, 2500A, 480V, 3, 2500AT, 65kAIC, SE RATED, OPEN/DELAYED, 100%, LSIG, ERMS | GENBH100 | -
CON00300 | CON | ELEVATOR, PANEL | UPSBH110 | -
CRA00300 | CRA | - | GENBH100 | -
ELPBH110 | ELP | - | MSBBH110 | -
ELPBH210 | ELP | - | MSBBH110 | -
ELPBH320 | ELP | - | MSBBH110 | -
ELPBH410 | ELP | - | MSBBH110 | -
ELPBH510 | ELP | - | MSBBH110 | -
ELPBH650 | ELP | - | MSBBH110 | -
ELPBH710 | ELP | - | MSBBH110 | -
ELPBH810 | ELP | - | MSBBH110 | -
ELPBH980 | ELP | - | MSBBH110 | -
EPPBH120 | EPP | - | MSBBH110 | -
EPPBH230 | EPP | - | MSBBH110 | -
EPPBH320 | EPP | - | MSBBH110 | -
EPPBH440 | EPP | - | MSBBH110 | -
EPPBH550 | EPP | - | MSBBH110 | -
EPPBH660 | EPP | - | MSBBH110 | -
EPPBH770 | EPP | - | MSBBH110 | -
EPPBH870 | EPP | - | MSBBH110 | -
EPPBH980 | EPP | - | MSBBH110 | -
GENBH100 | GEN | 1750kW/2187.5KVA, 480Y/277V, 3P, 4W, 0.80PF, 750kW, PANEL | - | -
MSBAH110 | MSB | - | GENBH100 | -
MSBBH110 | MSB | 2500A, 480Y/277V, 3, , 4W, 65kAIC, 2500AF, 2500AT, 100%, LSIG | ATSBH110 | -
TRNBH110 | TRN | AUTOMATIC TRANSFER | GENBH100 | -
TRNBH210 | TRN | 480V:208Y/120, 75KVA, NEMA 1 | MSBBH110 | -
TRNBH310 | TRN | 480V:208Y/120, PANEL, 75KVA, NEMA 1 | MSBBH110 | -
TRNBH440 | TRN | 480V:208Y/120, 75KVA, NEMA 1, PANEL | MSBBH110 | -
TRNBH510 | TRN | 480V:208Y/120, PANEL, 75KVA, NEMA 1 | MSBBH110 | -
TRNBH670 | TRN | 480V:208Y/120, 75KVA, NEMA 1 | MSBBH110 | -
TRNBH710 | TRN | 480V:208Y/120, PANEL, 75KVA, NEMA 1 | MSBBH110 | -
TRNBH910 | TRN | 480V:208Y/120, PANEL, 75KVA, NEMA 1 | MSBBH110 | -
UPPBH110 | UPP | - | UPSBH110 | -
UPSBH110 | UPS | BIB 150A LSI, 80kVA/80kW, 480V, 3, 208Y/120V, 3, STATIC SWITCH, 65kAIC, 150A | - | -
BDT00600 | BDT | 2500A, 480V, 3, , 3W, N1, 65kAIC | GSBBZ110 | -
BSW00200 | BSW | - | BDT00600 | -
BSWBZ110 | BSW | 2500A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE | MBCBZ110 | -
BSWBZ210 | BSW | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE | BSWBZ110 | -
BSWBZ310 | BSW | 1600A, 480V, 3, , 3W, N1, 65kAIC, TYPE I-LINE | BSWBZ210 | -
CHLB1800 | CHL | - | MSBBZ110 | -
CRAB0103 | CRA | - | EPPBZ110 | -
CRAB0104 | CRA | - | EPPBZ210 | -
CRAB0203 | CRA | - | EPPBZ110 | -
CRAB0204 | CRA | - | EPPBZ210 | -
CRAB0303 | CRA | - | EPPBZ110 | -
CRAB0304 | CRA | - | EPPBZ210 | -
CRAB0403 | CRA | - | EPPBZ110 | -
CRAB0404 | CRA | - | EPPBZ210 | -
CRAB0503 | CRA | - | EPPBZ110 | -
CRAB0504 | CRA | - | EPPBZ210 | -
CRAB0603 | CRA | - | EPPBZ110 | -
CRAB0604 | CRA | - | EPPBZ210 | -
CRAB0703 | CRA | - | EPPBZ110 | -
CRAB0704 | CRA | - | EPPBZ210 | -
CRAB0803 | CRA | - | EPPBZ110 | -
CRAB0804 | CRA | - | EPPBZ210 | -
CRAB0903 | CRA | - | EPPBZ110 | -
CRAB0904 | CRA | - | EPPBZ210 | -
CRAB1003 | CRA | - | EPPBZ210 | -
CRAB1004 | CRA | - | EPPBZ210 | -
CRAB1103 | CRA | - | EPPBZ110 | -
CRAB1203 | CRA | - | EPPBZ110 | -
CRAB1204 | CRA | - | EPPBZ210 | -
CRAB1303 | CRA | - | EPPBZ110 | -
CRAB1304 | CRA | - | EPPBZ210 | -
CRAB1403 | CRA | - | EPPBZ110 | -
CRAB1404 | CRA | - | EPPBZ210 | -
CRAB1503 | CRA | - | EPPBZ110 | -
CRAB1504 | CRA | - | EPPBZ210 | -
CRAB1603 | CRA | - | EPPBZ110 | -
CRAB1604 | CRA | - | EPPBZ210 | -
CRAB2400 | CRA | - | MDPBZ110 | -
CRAB2500 | CRA | - | MDPBZ110 | -
ELPBZ110 | ELP | - | MDPBZ110 | -
EPPBZ110 | EPP | 150A, 480V, 3, , 3W, 35kAIC | EPPBZ210 | -
EPPBZ120 | EPP | - | MDPBZ110 | -
EPPBZ210 | EPP | 150A, 480V, 3, , 3W, 35kAIC | MDPBZ110 | -
GENBZ100 | GEN | 3000kW/3750KVA, 480Y/277V, 3 | - | -
GSBBC110 | GSB | - | GSBBZ110 | -
GSBBD110 | GSB | - | GSBBZ110 | -
GSBBZ110 | GSB | 4000A, 480Y/277V, 3, , 4W, 65kAIC, 4000AF, 4000AT, 100%, LSIG, ERMS, S.T.U. | GENBZ100 | -
MBCBZ110 | MBC | 2500AF, 2500AT, 2500A, 480V, 3, , 3W, 100kAIC, 100%, LSI, ERMS | UPSBZ110 | UPBBZ110
MDPBZ110 | MDP | 600A, 480V, 3, , 3W, 65kAIC | GSBBZ110 | -
MSBBZ110 | MSB | 4000A, 480Y/277V, 3, , 4W, 100kAIC, S.E. RATED, WOODWARD PLC BREAKER TRANSFER CONTROLLER, BREAKER TRANSFER IS DELAYED OPEN TRANSITION, 4000AF, 4000AT, 100% | GSBBZ110 | -
TRNBZ110 | TRN | - | GSBBZ110 | -
TRNBZ210 | TRN | 480V:208Y/120, 45KVA, NEMA 1, PANEL | MDPBZ110 | -
UPBBZ110 | UPB | - | UPSBZ110 | -
UPBBZ120 | UPB | - | UPSBZ210 | -
UPBBZ210 | UPB | - | UPSBZ110 | -
UPBBZ220 | UPB | - | UPSBZ210 | -
UPBBZ310 | UPB | - | UPSBZ110 | -
UPBBZ320 | UPB | - | UPSBZ210 | -
UPBBZ410 | UPB | - | UPSBZ110 | -
UPBBZ420 | UPB | - | UPSBZ210 | -
UPBBZ510 | UPB | - | UPSBZ110 | -
UPBBZ520 | UPB | - | UPSBZ210 | -
UPSBZ110 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MSBBZ110 | -
UPSBZ210 | UPS | 1000kVA/1000kW, 480Y/277V, 3 | MSBBZ110 | -